## List of compulsory requirements
Start of table |  |  |  |  | End of table right side
SUBCLAUSE NO. | Level | REQUIRED |  | OFFERED
4 | 1 | SCOPE OF WORK
4.3 | 2 | SCOPE OF SUPPLY & SERVICE
4.3.1.3 | 4 | Racks for battery installation: The racks shall be PASSONI ALPHA rack ©, earthquake proof, white epoxy powder coated with corrosion resistance and good electrical isolation in accordance with Manufacturer standard, suitable for direct floor fastening by screws. The racks shall be able to arrange the cells in horizontal position in 3 or more levels (maximum height: 1.60 [m]).
4.3.3 | 3 | In addition to the a/m equipment the Bidder shall provide the services and goods listed in the following sub-articles stated in the proposal. Field personnel provided by the Bidder shall be capable, qualified and able to perform the duties required to the satisfaction of the Purchaser:
4.3.3.1 | 4 | Samples©: This service shall be included in the Firm Price of the batteries( item 1) . The bidder is required to provide , as a compulsory requirement, 2 (two) fully charged cells of the proposed type of the batteries (item 1) for carrying out the sample tests in the Purchaser's laboratory. in addition to bidder's technical documents. © The Bidder shall submit not later than one (1) month after technical proposal 2 (two) fully charged cells of the proposed type of the batteries (item 1) for carrying out the sample tests in the Purchaser's laboratory.
6.2 | 2 | Interchangeability ©
6.2.1 | 3 | Battery components of the same type, ratings and year of manufacture shall be respectively interchangeable with each other, both electrically and mechanically. Like parts shall be entirely interchangeable between components of the same rating, and when so interchanged, shall perform their function equally well in every respect.
10 | 1 | Tests
10.2.1 | 3 | Type tests reports shall be submitted with the proposal | Yes©
10.3.2 | 3 | Acceptance tests shall be performed in accordance with IEC 60896-21 for 100% of supplied batteries as defined in Appendix № 1. The equipment can be delivered only after Purchaser's approval of all relevant acceptance test reports | Yes©
11 | 1 | DESIGN AND CONSTRUCTION
11.1 | 2 | Batteries general requirements
11.1.1 | 3 | Batteries shall be of OPzV Gel Valve Regulated Lead-Acid type, designed for service in fixed location, suitable for indoor installation, permanently connected to the load and to the DC power supply | yes ©
11.1.4 | 3 | The batteries shall be supplied to I.E.Co fully charged, complete with all accessories and appurtenances (vent plugs, inter-cell connections, pole terminals, racks for battery installation, etc.) to form a complete battery. | Yes ©
11.1.5 | 3 | Field assembly of the batteries should be done by bolting. Field welding is not acceptable. | Yes ©
11.1.8 | 3 | The batteries shall be designed and constructed for long lifetime according to EUROBAT definition | Yes ©
11.1.11 | 3 | Links between cells should be fully insulated (rubber molded solid cooper), including bolts, and should be made by screw connection (bolts only, without nuts). | Yes ©
11.1.13 | 3 | The cell connectors (terminals) will have adequate current-carrying capacity and should be 100% gas- and electrolyte tight, corrosion free sliding-pole plastic part with gasket, without ferrous insert. Terminal screw should be with insulating head and provision for single cell voltage measurement. Terminals should be protected: first - IP25 according to IEC 60529, second - against accidental contact in accordance with VBG4 (see picture for example). | Yes ©
11.1.15 | 3 | Each battery shall consist of 106 cells. | Yes ©
11.1.16 | 3 | The cells will allow horizontal installation. | Yes ©
11.1.18 | 3 | Construction of cell terminals and connectors will allow easy voltage and impedance measurements. | Yes ©
11.1.19 | 3 | The racks for battery installation shall be PASSONI ALPHA racks©, earthquake proof for moderate level (0.5g), plastic coated with corrosion resistance and good electrical isolation in accordance with Manufacturer standard, suitable for direct floor fastening by screws. | Yes ©
11.1.20 | 3 | The batteries shall be provided with a Battery Management System (BMS). See clause 11.8. | Yes ©
11.1.21 | 3 | The Contractor shall provide the dismantling and evacuation of the old batteries from the Purchaser's sites – in parallel with the supplying and erection of the new batteries on the same sites. | Yes ©
11.1.22 | 3 | for lifting services The contractor will anticipate that battery room is situated on upper floors within the building. To accommodate the removal of existing batteries and racks and installation of new ones, the contractor will arrange and provide, a crane or other appropriate lifting equipment | Yes ©
11.2 | 2 | Batteries samples
11.2.1 | 3 | 2 (two) fully charged cells of the proposed type of the batteries shall be submitted not later than one (1) month after technical proposal submitting for carrying out a tests in Purchaser's laboratory© | Yes ©
11.4 | 2 | Battery data
11.4.1 | 3 | Battery Amp-Hour “discharge capacities” for the 10 hours time periods assuming an initial electrolyte temperature of 25°C and 1.80 final volt per cell in accordance with IEC 60896-21: ITEM 1 | 175 [AH]©
11.5 | 2 | Cell data
11.5.1 | 3 | Cell's terminals shall be of "female pole type" (terminal with internal screwing for bolt inserts) | Yes ©
11.5.2 | 3 | Connecting bolts, nuts and washers shall be of fully insulated type. | Yes ©
11.8 | 2 | Battery Management System
11.8.1 | 3 | Each battery shall be equipped with a battery management system (BMS) for measuring, monitoring and indication of voltages, currents, power, external and internal temperature, internal resistance and battery parameters control, with communication facilities. | Yes ©
11.8.2 | 3 | The BMS shall provide continuous visibility (LCD and LED indications) and remote indication (via dry alarm contacts) of battery health and status. | Yes ©
11.8.6 | 3 | the “End User License Agreement” and “Software/Firmware Maintenance Agreement” shall be submitted with proposal and shall be included in the contract. | Yes ©
11.8.6.1 | 4 | The license for BMS software will be for unlimited users and without expiration date | Yes ©
11.8.7 | 3 | In case of battery fault detection, the BMS will close "Battery Fault" alarm contacts for remote alarm annunciation. | Yes ©
11.8.8 | 3 | The BMS shall be installed at a distance not greater than 50 meters from the batteries room | Yes ©
11.8.9 | 3 | The BMS or a controller provided and connected with the BMS shall allow notifications transfer via 7 dry contacts through outputs card working at 60VDC | Yes ©
11.8.9.1 | 4 | The BMS shall indicate via 7 dry alarms of the following:
11.8.9.1.1 | 5 | the firt dry alarm shall indicate of communication failure / error | yes
11.8.9.1.2 | 5 | the second dry alarm shall indicate of single cell voltage error | yes
11.8.9.1.3 | 5 | the 3th dry alarm shall indicate of a total voltage error | yes
11.8.9.1.4 | 5 | the 4th dry alarm shall indicate of an internal resistance error | yes
11.8.9.1.5 | 5 | the 5th dry alarm shall indicate of current error | yes
11.8.9.1.6 | 5 | the 6th dry alarm shall indicate of an external temprture error | yes
11.8.9.1.7 | 5 | the 7th dry alarm shall indicate of an internal temprture error | yes
11.8.9.1.8 | 5 | if needed the dry contacts could be connected togther for signaling as a common failure | yes
11.8.12 | 3 | Mechanical and electrical Design Requirements:
11.8.12.8 | 4 | The BMS is to be supplied as a complete system that includes all the necessary ancillary equipment. | Yes ©
11.8.10.9 | 4 | BMS's Signal and alarm outputs will have the following characteristics:
11.8.12.9.6 | 5 | Serial data communication interface for a portable PC for BMS parameter settings and data download (Yes / No) | Yes ©
11.8.14 | 3 | Cyber and information security©
11.8.14.1 | 4 | The contractor shall submit with the proposal, filled in cyber security requirements-Critical isulated network product - appendix 5. the appendix must be completely filled in, signed by the bidder and submitted with the proposal © | Yes ©
11.8.14.2 | 4 | The contractor shall submit with the proposal, filled in Software Requirement Oct2024 - appendix 6. the appendix must be completely filled in, signed by the bidder and submitted with the proposal © | Yes ©
11.8.14.3 | 4 | The contractor shall submit with the proposal, filled in Guiding questions on security of a critical network product - appendix 7. the appendix must be completely filled in, signed by the bidder and submitted with the proposal © | Yes ©
11.9 | 2 | Racks for battery installation
11.9.1 | 3 | the term 'racks for battery installation' refers to the complete set of rack units that accommodate all battery cells, the Battery Management System (BMS), and the required accessories. | Yes ©
11.9.2 | 3 | The racks shall be PASSONI ALPHA rack© | Yes ©
11.9.5 | 3 | in case of order, the bidder shall submit a detailed design of the racks in the battery room also a detalied plan of the arrangement of the batteries and battery mangement system on the stands .bidder shall submit calculations of the required ventilation in the room for idial opration of the batteries and a safe environment, all in acordance with the four types of battery room plans in appendix 4 | Yes ©
12 | 1 | DELIVERY, PACKING, SHIPMENT AND STORAGE
12.6 | 2 | The spare parts and special tools shall be packed separately and a detailed packing list shall be sent. The spare part set shall include (but not exclude all another spare parts): bolts, links between cells, toping plugs (corks) – as 10% addition to required quantity | Yes ©
14 | 1 | QUALITY CONTROL
14.1 | 2 | The Bidder shall submit with his proposal a preliminary Inspection and Test Plan (I&T Plan) | Yes ©
16 | 1 | WARRANTY
16.1 | 2 | The total warranty period shall be 72 (seventy two) months (6 years) starting from the date of putting the battery into operation in the Purchaser’s site. | Yes ©
16.1.1 | 3 | During this period the battery / cell(s) shall be considered as faulty if: -the battery / cell(s) capacity is less than 80% of the rated battery / cell(s) capacity, and/or -the cell(s) fully " floated operated" voltage is less than 2.2 volt per cell, and/ or -corrosion occurs on the cell(s) terminals. -failure or inaccuracy of measuring instruments | Yes ©
16.2 | 2 | in case of breakdowns or any dis-orderly function of the batteries and its overall system, the bidder shall arrange a qualified Field personnel to adjust, repair or replace the necessary components until the battery system is performing according to IEC's requirements. Field service shall be provided within a week or according to IEC's approval" | Yes ©
16.3 | 2 | During the total warranty period the contractor agrees promptly (within 7 working days after written notice by the purchaser) and at its own expense to repair or replace the faulty battery / cell(s) including all needed operations (dismantling, transportation and on site erection after repairing/ replacement). In case that the number of fault cells in the same battery shall be equal or more than 5, the whole battery shall be replaced. | Yes ©
16.4 | 2 | In case the replacement of the faulty battery/cells is needed, the replacement shall be provided on Purchaser's sites. The faulty battery/cells shall be replaced by the proper one. The Contractor shall be responsible for all maintenance works, needed for these batteries/cells during the stocking | Yes ©
16.5 | 2 | If the Contractor does not repair or replace any such part within 7 working days after written notice by the Purchaser, the Purchaser may repair and/or replace it at Contractor’s expense without prejudice to any other rights of the Purchaser | Yes ©
16.6 | 2 | The above warranties shall also apply to any replacement parts including the steel racks, the Battery Management System (BMS), inter-cell connectors, etc. | Yes ©
16.7 | 2 | Notwithstanding the provisions above, the warranty time period on the batteries shall be extended by a period equal to the period of duration for which the battery is out of operation due to the fault of the Contractor or any other breach of that warranted herein. | Yes ©
17 | 1 | TECHNICAL DOCUMENTS TO ACCOMPANY THE PROPOSAL
17.2 | 2 | The proposal shall include, at least, the following documents: | yes ©
17.2.1 | 3 | Annexure B - STR- 1791 – fill in all clauses that requires an answer
17.2.2 | 3 | Dimension drawings of the proposed Battery cells, giving principal dimensions, weights, etc.
17.2.3 | 3 | Drawing of the connections between cells including details of the terminals and connectors
17.2.4 | 3 | Charge and discharge characteristic curves of new battery
17.2.5 | 3 | Thermal runaway sensitivity characteristic curves at 2.45 & 2.6 (Vpc).
17.2.6 | 3 | Description and drawings of provisions for installing the batteries (including cells arrangement on the racks) on the concrete floor in the battery room
17.2.7 | 3 | Reliability, availability, maintainability and safety (RMS) report (Appendix № 3)
17.2.8 | 3 | Description of the Bidder's representation in Israel to prove ability to provide the maintenance services, as described in specification STR-1791
17.2.9 | 3 | A list of recommended spare parts (including total quantities) for the amount of the batteries, indicated in this specification.
17.2.10 | 3 | An example of routine test report for offered types of the batteries
17.2.11 | 3 | Drawings of the proposed Battery Management System, giving principal dimensions, weights, installing and connection details, etc.
17.2.12 | 3 | Steel racks dimension drawing, description of racks arrangement indicating clearances between racks of the same battery and between racks of different batteries, general information and drawings covering the principle design of the modular racks.
17.2.13 | 3 | Steel racks seismic qualification report.
17.2.14 | 3 | List of accessories and fittings with short description, technical data and catalogues
17.2.15 | 3 | Drawing of nameplate (cell's marking)
17.2.16 | 3 | Drawing of the steel racks nameplate
17.2.17 | 3 | Type tests reports (authority, number and date) for offered types of the battery, including test circuit, instruments used and description of method, calibration certificate
17.2.18 | 3 | Customer list for the last three (3) years, with sum for each year (number of units, date of supply, Purchaser)
17.2.19 | 3 | A list of all necessary maintenance work for each service period (for example: for period of 3 months, 6 months, one year etc.)
17.2.20 | 3 | Complete instruction book as may be required for storage, erection, operating and maintaining of the battery, and for ordering spare parts. Instruction book shall also include such drawings, list of parts, etc., as may be required
17.2.21 | 3 | Complete instruction book of the Battery management system for erection, operating and maintaining of the system, including drawings, list of parts, etc. as may be required
17.2.22 | 3 | Certificate for approval of the Quality Assurance System according to ISO 9001 Standard given by an Authorized Inspection Agency
17.2.23 | 3 | Quality plan during manufacture
17.2.24 | 3 | Acceptance test procedures for materials and sub-assembles
17.2.25 | 3 | Inspection and test procedures
17.2.26 | 3 | a preliminary inspection and test plan ( I&T PLAN)
17.2.27 | 3 | a filled in and signed cyber security requirements-Critical isulated network product - appendix 5.
17.2.28 | 3 | a filled in and signed Software Requirement Oct2024 - appendix 6.
17.2.29 | 3 | a filled in and signed Guiding questions on security of a critical network product - appendix 7.
End of table