# List of Required Tests and Tests Reports

## Table 1 – Type and Special Tests Reports for Earthing Transformer (ET) type _____________

| № | Description | IEC 60076-6 /2007 |  | Test plant | Date of test | Test report |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Clause | Value |  |  | № | Value |  |
| 1.* | Dielectric Tests (type tests): | 10.9.3 10.9.7 |  |  |  |  |  |  |
| 1.1* | Lightning impulse test acc. to IEC 60076-3 /2018 cl.13 |  |  |  |  |  |  |  |
| 2.* | Temperature rise tests (type tests): | 10.9.3 10.9.6 |  |  |  |  |  |  |
| 2.1* | Temperature rise test for ET (item 1) at rated continuous neutral current of 120 A acc. to IEC 60076-2 /2011 cl.6,7 for: |  |  |  |  |  |  |  |
| a. | Top insulating liquid (0C) |  |  |  |  |  |  |  |
| b. | Average winding (0C) |  |  |  |  |  |  |  |
| c. | Hot-spot winding (0C) |  |  |  |  |  |  |  |

* This Type test shall be performed by one of the neutral laboratories - Member of the STL (Short-Circuit Testing Liaison) international forum.

Table 1 – Type and Special Tests Reports for Earthing Transformer (ET) type _____________ (cont.)

| № | Description | IEC 60076-6 /2007 |  | Test plant | Date of test | Test report |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Clause | Value |  |  | № | Value |  |
| 2.2* | Temperature rise test for ET (item 1) at rated 1 (one) hour neutral current of 350 A acc. to IEC 60076-2 /2011 cl.6,7 for: |  |  |  |  |  |  |  |
| a. | Top insulating liquid (K) |  |  |  |  |  |  |  |
| b. | Average winding (K) |  |  |  |  |  |  |  |
| c. | Hot-spot winding (K) |  |  |  |  |  |  |  |
| 3.* | Demonstration of ability to withstand rated short-time neutral current (special test): | 10.9.4 10.9.8 |  |  |  |  |  |  |
| 3.1* | ET (Item 1) with rated short –time neutral current of 3300 A, rated duration 10 sec and max. windings temperature rise up to 250 K |  |  |  |  |  |  |  |

* This Type test shall be performed by one of the neutral laboratories - Member of the STL (Short-Circuit Testing Liaison) international forum.

Table 1 – Type and Special Tests Reports for Earthing Transformer (ET) type _____________ (cont.)

| № | Description | IEC 60076-6 /2007 |  | Test plant | Date of test | Test report |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Clause | Value |  |  | № | Value |  |
| 4. | Measurement of no-load losses at maximum operating voltage (36 kV) acc. to IEC 60076-1 /2011 (special test) for ET (Item 1) | 10.9.4 |  |  |  |  |  |  |
| 5. | Measurement of load losses at 75°C and rated continuous neutral current of 120A for ET (item 1) |  |  |  |  |  |  |  |
| 6. | Measurement of load losses at 75°C and rated 1 (one) hour neutral current of 350 A for ET (item 1) |  |  |  |  |  |  |  |

Table 1 – Type and Special Tests Reports for Earthing Transformer (ET) type _____________ (cont.)

| № | Description | IEC 60076-6 /2007 |  | Test plant | Date of test | Test report |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Clause | Value |  |  | № | Value |  |
| 7. | Measurement of acoustic sound level acc. to IEC 60076-10 /2016 (special test): | 10.9.4 |  |  |  |  |  |  |
| 7.1 | Sound pressure level under no-load at rated voltage and rated frequency at 0.3 m from the principal radiating surface of ET (item 1) |  |  |  |  |  |  |  |
| 7.2 | Sound pressure level at rated continuous current of 120 A, rated voltage and rated frequency at 0.3 m from the principal radiating surface of ET (item 1) |  |  |  |  |  |  |  |
| 8. | Type tests for line and neutral bushings shall be performed and submitted acc. to IEC 60137 /2017 |  |  |  |  |  |  |  |
| 9. | Type tests for bushing current transformer shall be performed and submitted acc. to IEC 61869-2 /2012 |  |  |  |  |  |  |  |

Table 1 – Type and Special Tests Reports for Earthing Transformer (ET) type _____________ (cont.)

| № | Description | IEC 60076-6 /2007 |  | Test plant | Date of test | Test report |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Clause | Value |  |  | № | Value |  |
| 10. | Verification of degree of protection (IP code) of control box shall be performed and submitted acc. to IEC 60529 /2013 |  |  |  |  |  |  |  |
| 11. | Dielectric tests on auxiliary and control circuits shall be performed and submitted acc. to IEC 62271-1 /2017+A1 2021 cl. 7.2.11 & 7.10.5 |  |  |  |  |  |  |  |
| 12. | Type tests for all other accessories shall be performed and submitted in accordance with relevant standards |  |  |  |  |  |  |  |

Table 1 – Type and Special Tests Reports for Earthing Transformer (ET) type _____________ (cont.)

| № | Description | IEC 60076-6 /2007 |  | Test plant | Date of test | Test report |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Clause | Value |  |  | № | Value |  |
| 13. | Equipment qualification to prove seismic withstand acc. to IEEE Std 693 /2018 Required seismic qualification level – moderate level. Required seismic qualification methods: - Transformer tank and bushings – by inherently acceptable acc. to IEEE Std 693 /2018 Annex. D. - Control and terminal boxes – by static analysis acc. to IEEE Std 693 /2018 Annex. L. Seismic analysis-qualification reports shall be prepared and supplied by the Contractor to the Purchaser acc. to IEEE Std 693-2018 |  |  |  |  |  |  |  |

## Table 2 – Routing Tests Reports for Earthing Transformer (ET) type _____________

| № | Description | IEC 60076-6 /2007 |  | Test plant | Date of test | Test report |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Clause | Value |  |  | № | Value |  |
| 1. | Measurement of winding resistance acc. to IEC 60076-1 /2011 cl. 11.2 | 10.9.2 |  |  |  |  |  |  |
| 2. | Measurement of zero-sequence impedance | 10.9.2 10.9.5 |  |  |  |  |  |  |
| 3. | Measurement of no-load loss and current acc. to IEC 60076-1 /2011 cl. 11.5 | 10.9.2 |  |  |  |  |  |  |
| 4. | Dielectric tests: | 10.9.2 10.9.7 |  |  |  |  |  |  |
| 4.1 | Separate source a.c. withstand voltage test acc. to IEC 60076-3 /2018 cl. 10 |  |  |  |  |  |  |  |
| 4.2 | Induced a.c. withstand voltage test acc. to IEC 60076-3 /2018 cl. 11 |  |  |  |  |  |  |  |
| 5. | Leak testing with pressure for liquid-immersed ET (tightness test) acc. to IEC 60076-1 /2011 cl. 11.1.2 and 11.8 |  |  |  |  |  |  |  |
| 6. | Check of the ratio and polarity of built-in current transformer acc. to IEC 60076-1 /2011 cl. 11.1.2 |  |  |  |  |  |  |  |

Table 2 – Routing Tests Reports for Earthing Transformer (ET) type _____________(cont.)

| № | Description | IEC 60076-6 /2007 |  | Test plant | Date of test | Test report |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Clause | Value |  |  | № | Value |  |
| 7. | Check of core and frame insulation for liquid-immersed ET acc. to IEC 60076-1 /2011 cl. 11.1.2 and 11.12 |  |  |  |  |  |  |  |
| 8. | Routine tests for line and neutral bushings shall be performed and submitted acc. to IEC 60137 /2017 |  |  |  |  |  |  |  |
| 9. | Routine tests for bushing current transformer shall be performed and submitted acc. to IEC 61869-2 /2012 |  |  |  |  |  |  |  |
| 10. | Routine tests on auxiliary and control circuits shall be performed and submitted acc. to IEC 62271-1 /2017+A1 2021 cl. 8.3 |  |  |  |  |  |  |  |