26/04/2026

659-0000613-2026

Subject: RFI – Auxiliary Relays and Bases

- PURCHASER:	The Israel Electric Corporation Limited.

- SCOPE OF WORK:

  - General

The Israel Electric Corporation (IECo) intends to procure auxiliary electromechanical relays and their bases for use in control, tripping, and signaling applications in high-voltage substations.

  - Scope of work

Supply, testing, and delivery of auxiliary relays and bases according to the technical requirements specified in this RFI. The relays shall comply with international standards (IEC, IEEE) and meet the operational and environmental conditions required for substation applications.

- TECHNICAL REQUIREMENTS

  - General

The auxiliary relays shall be electromechanical type, suitable for tripping, control, and signaling functions in high-voltage substations. All relays and bases shall comply with the latest IEC and IEEE standards.

  - Design Guidelines

- Relays shall be heavy-duty or medium-duty as specified, with bridge or twin contacts for high reliability.

- Mounting options: Panel base, Terminal base, and DIN rail (optional for certain items).

- Wiring shall be connected to the base, not the relay, allowing easy replacement without rewiring.

- Bases shall allow secure fastening and wiring via screw or locking clip (disconnection only with a tool).

3.3 Electrical Parameters

- Nominal Coil Voltage: 24VDC, 48VDC, 60VDC, 220VDC, 230VAC (depending on category).

- Operating Range: 80–110% of nominal voltage.

- Contact Configuration: 3CO, 4CO, 6CO, 7CO or equivalent NO/NC combinations.

- Switching Capacity:

  - Heavy-duty: Make 30A (0.2s), Carry 10A continuous, Break DC 500W resistive / 200W inductive.

  - Medium-duty: Make 30A (0.2s), Carry 5A continuous, Break DC 250W resistive / 100W inductive.

  - Light-duty signaling: Make 5A, Carry 3A continuous, Break DC 30W resistive / 15W inductive.

3.4 Insulation and Withstand

- Insulation resistance: >100 MΩ at 500 VDC.

- Dielectric withstand: 2 kV RMS for 1 minute between circuits and earth.

- Impulse withstand: 5 kV peak, 1.2/50 μs.

3.5 Environmental Conditions

- Operating temperature: –10°C to +55°C.

- Humidity: up to 95% for 30 days.

- Altitude: up to 2000 m above sea level.

3.6 Standards Compliance

Relays shall comply with:

- IEC 61810 (General requirements and reliability)

- IEC 60255 (Insulation coordination and tests)

- IEEE C37.90 (Relay systems for electric power apparatus)

- RELAY CATEGORIES (BASKETS)

| type | Nominal Coil Voltage | Required Contact Configuration | item |  |
| --- | --- | --- | --- | --- |
| Bi-stable Heavy-Duty Relay MEDIUM SIZE | 220VDC | 4CO or 3NO+3NC | 1.1 | Basket 1 |
| Bi-stable Heavy-Duty Relay MEDIUM SIZE | 60VDC | 4CO or 3NO+3NC | 1.2 |  |
| Bi-stable Heavy-Duty Relay LARGE SIZE | 220VDC | 7CO or 5NO+5NC | 2.1 |  |
| Bi-stable Heavy-Duty Relay LARGE SIZE | 60VDC | 7CO or 5NO+5NC | 2.2 |  |
| Heavy-Duty Relay MEDIUM SIZE | 220VDC | 3CO or 2NO+2NC | 3.1 |  |
| Heavy-Duty Relay MEDIUM SIZE | 60VDC | 3CO or 2NO+2NC | 3.2 |  |
| Heavy-Duty Relay LARGE SIZE | 220VDC | 6CO or 4NO+4NC | 4.1 |  |
| Heavy-Duty Relay LARGE SIZE | 60VDC | 6CO or 4NO+4NC | 4.2 |  |

| type | Nominal Coil Voltage | Required Contact Configuration | item |  |
| --- | --- | --- | --- | --- |
| MEDIUM-Duty Relay MEDIUM SIZE | 220VDC | 3CO or 2NO+2NC | 5.1 | Basket 2 |
| MEDIUM-Duty Relay MEDIUM SIZE | 60VDC | 3CO or 2NO+2NC | 5.2 |  |
| MEDIUM-Duty Relay MEDIUM SIZE | 48VDC | 3CO or 2NO+2NC | 5.3 |  |
| MEDIUM-Duty Relay LARGE SIZE | 220VDC | 6CO or 4NO+4NC | 6.1 |  |
| MEDIUM-Duty Relay LARGE SIZE | 60VDC | 6CO or 4NO+4NC | 6.2 |  |

| type | Nominal Coil Voltage | Required Contact Configuration | item |  |
| --- | --- | --- | --- | --- |
| FAST MEDIUM-Duty Relay MEDIUM SIZE | 220VDC | 3CO or 2NO+2NC | 7.1 | Basket 3 |
| FAST MEDIUM-Duty Relay MEDIUM SIZE | 60VDC | 3CO or 2NO+2NC | 7.2 |  |
| FAST MEDIUM-Duty Relay LARGE SIZE | 220VDC | 6CO or 4NO+4NC | 8.1 |  |
| FAST MEDIUM-Duty Relay LARGE SIZE | 60VDC | 6CO or 4NO+4NC | 8.2 |  |

| type | Nominal Coil Voltage | Required Contact Configuration | item |  |
| --- | --- | --- | --- | --- |
| Flag Medium-Duty Relay – Medium Size | 220VDC | 3CO or 2NO+2NC | 9.1 | Basket 4 |
| Flag Medium-Duty Relay – Medium Size | 60VDC | 3CO or 2NO+2NC | 9.2 |  |

| type | Nominal Coil Voltage | Required Contact Configuration | item |  |
| --- | --- | --- | --- | --- |
| LIGHT DUTY | 220VDC | 4CO or 3NO+3NC+ Indication upon coil energization | 10.1 | Basket 5 |
| LIGHT DUTY | 60VDC | 4CO or 3NO+3NC+ Indication upon coil energization | 10.2 |  |
| LIGHT DUTY | 24VDC | 4CO or 3NO+3NC+ Indication upon coil energization | 10.3 |  |
| LIGHT DUTY | 230VAC | 4CO or 3NO+3NC+ Indication upon coil energization | 10.4 |  |

Note: Suppliers may submit proposals for selected baskets only. It is not mandatory to offer items from all baskets.

Please mark the baskets you are offering by placing a ✓ in the relevant box:

| Basket No. | Offered (✓) |
| --- | --- |
| Basket 1 |  |
| Basket 2 |  |
| Basket 3 |  |
| Basket 4 |  |
| Basket 5 |  |

- Estimated Quantities for 5 Years

| Description | Item No. | Estimated Quantity | Confirm |
| --- | --- | --- | --- |
| Basket 1 |  |  |  |
| # Bi-stable Heavy-duty Relay-Medium Size |  |  |  |
| ## Coil nominal Voltage 220VDC © | ## 1.1 | 230 |  |
| ## Coil nominal Voltage 60VDC © | ## 1.2 | 230 |  |
| Terminal Base Mounting © | 1.3 | 230 |  |
| Panel Base Mounting © | 1.4 | 230 |  |
| ### Bi-stable Heavy-duty Relay-Large Size |  |  |  |
| ### Coil nominal Voltage 220VDC © | ### 2.1 | ### 115 |  |
| ### Coil nominal Voltage 60VDC © | ### 2.2 | ### 115 |  |
| ### Terminal Base Mounting © | ### 2.3 | ### 115 |  |
| ### Panel Base Mounting © | ### 2.4 | ### 115 |  |
| ### Heavy duty Relay-Medium Size |  |  |  |
| ### Coil nominal Voltage 220VDC © | ### 3.1 | ### 230 |  |
| ### Coil nominal Voltage 60VDC © | ### 3.2 | ### 230 |  |
| ### Terminal Base Mounting © | ### 3.3 | ### 230 |  |
| ### Panel Base Mounting © | ### 3.4 | ### 230 |  |
| ### Heavy duty Relay-Large Size |  |  |  |
| ### Coil nominal Voltage 220VDC © | ### 4.1 | ### 115 |  |
| ### Coil nominal Voltage 60VDC © | ### 4.2 | ### 115 |  |
| ### Terminal Base Mounting © | ### 4.3 | ### 115 |  |
| ### Panel Base Mounting © | ### 4.4 | ### 115 |  |
| ### Basket 2 |  |  |  |
| ### Medium Duty-Medium Size |  |  |  |
| ### Coil nominal Voltage 220VDC © | ### 5.1 | ### 230 |  |
| ### Coil nominal Voltage 60VDC © | ### 5.2 | ### 230 |  |
| ### Coil nominal Voltage 48VDC © | ### 5.3 | ### 115 |  |
| ### Terminal Base Mounting © | ### 5.4 | ### 288 |  |
| ### Panel Base Mounting © | ### 5.5 | ### 288 |  |
| ### Medium Duty-Large Size |  |  |  |
| ### Coil nominal Voltage 220VDC © | ### 6.1 | ### 115 |  |
| ### Coil nominal Voltage 60VDC © | ### 6.2 | ### 115 |  |
| ### Terminal Base Mounting © | ### 6.3 | ### 115 |  |
| ### Panel Base Mounting © | ### 6.4 | ### 115 |  |
| ### Basket 3 |  |  |  |
| ### Fast Medium Duty-Medium Size |  |  |  |
| ### Coil nominal Voltage 220VDC © | ### 7.1 | ### 230 |  |
| ### Coil nominal Voltage 60VDC © | ### 7.2 | ### 230 |  |
| ### Terminal Base Mounting © | ### 7.3 | ### 230 |  |
| ### Panel Base Mounting © | ### 7.4 | ### 230 |  |
| ### Fast Medium Duty-Large Size |  |  |  |
| ### Coil nominal Voltage 220VDC © | ### 8.1 | ### 115 |  |
| ### Coil nominal Voltage 60VDC © | ### 8.2 | ### 115 |  |
| ### Terminal Base Mounting © | ### 8.3 | ### 115 |  |
| ### Panel Base Mounting © | ### 8.4 | ### 115 |  |
| ### Basket 4 |  |  |  |
| ### Flag Relay Medium Duty-Medium Size |  |  |  |
| ### Coil nominal Voltage 220VDC © | ### 9.1 | ### 115 |  |
| ### Coil nominal Voltage 60VDC © | ### 9.2 | ### 115 |  |
| ### Terminal Base Mounting © | ### 9.3 | ### 115 |  |
| ### Panel Base Mounting © | ### 9.4 | ### 115 |  |
| ### Basket 5 |  |  |  |
| ### Light Duty |  |  |  |
| ### Coil nominal Voltage 220VDC © | ### 10.1 | ### 1150 |  |
| ### Coil nominal Voltage 60VDC © | ### 10.2 | ### 3220 |  |
| ### Coil nominal Voltage 24VDC © | ### 10.3 | ### 115 |  |
| ### Coil nominal Voltage 230VAC © | ### 10.4 | ### 115 |  |
| ### DIN RAIL 4 mm Disconnect Terminal mounting © | ### 10.7 | ### 4600 |  |

- Delivery Time

The supplier shall specify the delivery time for each offered item, calculated from the date of purchase order issuance. Delivery time shall be expressed in calendar weeks and shall include all necessary manufacturing, testing, and shipping activities.

Please indicate:

Standard delivery time for each basket .

| Basket No. | Delivery Time (weeks) |
| --- | --- |

- Price Estimation and Offered Models

Please complete the table below for each item you are offering. Include the following details:

| Basket No. | Manufacturer Name | Catalog Number | Product Family / Model | Estimated Unit Price |
| --- | --- | --- | --- | --- |

Closing Notes

- Please ensure all requested tables in this RFI are fully completed.

- Refer to Basket and Item numbers provided in previous sections.

- Attach datasheets and technical documentation for all offered models.

- Prices shall exclude VAT but include delivery to IEC warehouse.

- The purchaser reserves the right to request additional clarifications or documentation.

| Proposer’s address: |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Manufacturer address: |  |  |  |  |  |
| Proposer’s Fax. No.: |  |  |  | Tel. No. : |  |
| Date: |  |  | Signature: |  |  |